## 1)RING #1
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET
| RING # 01 (DTS # 02 PNO: A10 & A20) | [9 empty] | AUGUST - 2024 |  |  | PAGE 1 OF 19
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| Mosque | DTS # 02 | XXX |  | 10 | 10 | 9 | 11.03 | XXX
|  | TX-1 | 230 | 5662780 | 11 | - | 10 |  | 164 | 224 | 242 | 416 | 31/07/2024 08.45Hrs
|  | TX-2 | 170 | 1534820 | 8 | - | 7 |  | 176 | 176 | 236
|  | Fire Station | XXX |  | 0 | 0 | 0 |  | 3
| Fire Station | Mosque | XXX |  | OFF |  |  | 10.9 | XXX |  |  |  | 31/07/2024 09.15Hrs
|  | TX-1 | 380 | 466 | 16 | 13 | 16 |  | 295 | 383 | 291 | 416
TX-2
|  | TX-2 | 225 | 2898 | 9 | 8 | 7 |  | 280 | 140 | 161
|  | Substation#N3 | XXX |  | 24 | 18 | 20
| Substation # N3 | Fire Station | XXX |  | 28 | 20 | 25 | 10.94 | XXX
|  | TX-1 | 43 | 1113090 | 2 | 2 | 2 |  | 26 | 248 | 30 | 431 | 31/07/2024 09.50Hrs
|  | TX-2 | 2 | 402590 | 0 | 0 | 0 |  | 0 | 0 | 0
|  | D-Type | XXX |  | 30 | 22 | 27 |  | XXX
| D-Type | Substation#N3 | XXX |  | 24 | 20 | 20 | 10.9 | XXX |  |  |  | 31/07/2024 10.15Hrs
|  | TX-1 | 130 | 9815450 | 5 | - | 4 |  | 140 | 110 | 100 | 420
|  | TX-2 | 260 | 9636910 | 10 | - | 8 |  | 160 | 120 | 104
|  | Kahrama PS | 100 | 3453270 | 0 | - | 0 |  | XXX
|  | DTS # 02 | XXX |  | 38 | 33 | 29 |  | XXX

## 2)RING #2
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET
| RING # 02 (DTS # 02 PNO: A30 & A40) | [9 empty] | AUGUST - 2024 |  |  | PAGE 2 OF 19
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| Main Camp (New) | DTS # 02 | 169 | 3536438 | 7 | 7 | 7 | 10.89 | XXX
|  | TX-1 | 130 | 3514025 | 6 | 6 | 6 |  | 175 | 167 | 139 | 430 | 30/07/2024 13.10Hrs
|  | TX-2 | 43 | 1027013 | 1 | 1 | 1 |  | 0 | 0 | 0
|  | Escarpment | XXX |  | 0 | 0 | 0
| Escarpment | Main Camp New) | XXX |  | OFF |  |  | 10.8 | XXX
|  | TX-1 | 460 | 21981 | 20 | 21 | 19 |  | 561 | 506 | 475 | 415 | 30/07/2024 10.20Hrs
|  | TX-2 | 483 | 31641 | 23 | 24 | 24 |  | 603 | 602 | 595
|  | SS Bungalow | XXX |  | 43 | 44 | 44
| S.S.Bungalow | Escarpment | XXX |  | 48 | 42 | 44 | 10.8 | XXX
|  | TX-1 | 170 | 431910 | 7 | - | 7 |  | 184 | 188 | 200 | 415 | 30/07/2024 13.35Hrs
|  | TX-2 | 170 | 458830 | 7 | - | 7 |  | 168 | 188 | 176
|  | Supalite | XXX |  | 32 | 35 | 33
| Supalite | SS Bungalow | XXX |  |  |  |  | - | XXX
|  | TX-1 | 314 | 33506939 | XXX |  |  |  | 368 | 431 | 469 | 408 | 30/07/2024 13.20Hrs
|  | TX-2 | 303 | 32180744 | XXX |  |  |  | 377 | 411 | 457
|  | DTS # 02 | XXX | [5 empty] | XXX

## 3)RING #3
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET
| RING # 03 (DTS # 02 PNO: A50 & A60) | [9 empty] | AUGUST - 2024 |  |  | PAGE 3 OF 19
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| Hospital | DTS # 02 | 794 | 79529 | 41 | 42 | 40 | 10.8 | XXX
|  | TX-1 | 335 | 177 | 18 | 19 | 16 |  | 471 | 373 | 356 | 408 | 2024-07-29
|  | TX-2 | 220 | 4068 | 2 | 2 | 2 |  | 118 | 120 | 126 |  | 13.00HRS
|  | New Cinema | XXX |  | 23 | 24 | 23 |  | XXX
| New Cinema | Hospital | XXX |  | 18 | 18 | 18 | 10.8 | XXX
|  | TX-1 | 292 | 7029456 | 11 | 11 | 11 |  | 342 | 345 | 337 | 428 | 2024-07-29
|  | TX-2 | 153 | 3816314 | 6 | 6 | 6 |  | 179 | 160 | 160 | 430 | 10.50HRS
|  | New M.R.Club | XXX |  | 0 | 0 | 0 |  | XXX
| New M.R. Club | New Cinema | XXX |  | OFF |  |  | 10.81 | XXX
|  | TX-1 | 660 | 3437022 | 33 | 35 | 33 |  | 852 | 852 | 52 | 427 | 2024-07-29
|  | TX-2 | 730 | 6164894 | 36 | 37 | 34 |  | 939 | 807 | 775 | 427 | 13.20HRS
|  | DTS # 2 | 1345 | 8581422 | 70 | 73 | 68 |  | XXX

## 4)RING #4
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET
| RING # 04 (DTS # 01 PNO: A30 & A40) | [9 empty] | AUGUST - 2024 |  |  | PAGE 4 OF 19
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| F/Ball Pitch | DTS # 01 | 240 | 68424400 | 8 | - | 7 | 11.01 | XXX
|  | TX-1 | 120 | 352040 | 3 | - | 3 |  | 105 | 90 | 84 | 418 | 2024-07-29
|  | TX-2 | 120 | 5272770 | 3 | - | 4 |  | 98 | 91 | 98 |  | 09.53HRS
|  | Dk-5 | XXX |  | OFF
| DK-5 | Football Pitch | XXX |  | 0 | 0 | 0 | 11.01 | XXX
|  | TX-1 | 180 | 9241640 | 8 | - | 7 |  | 84 | 84 | 91 | 416 | 2024-07-29
|  | TX-2 | 260 | 9810620 | 10 | - | 10 |  | 224 | 294 | 301 |  | 09.13HRS
|  | DTS # 01 | XXX |  | 8 | 12 | 12 |  | XXX

## 5)RING #5
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET
| RING # 05 (DTS # 01 PNO: A50 & A60) | [9 empty] | AUGUST - 2024 |  |  | PAGE 5 OF 19
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| Dk5 Bungalows | DTS # 01 | 212 | 1327 | 16 | 15 | 16 | 11.25 | XXX
|  | TX-1 | 117 | 8931 | 7 | 7 | 7 |  | 74 | 110 | 137 | 414 | 2024-07-29
|  | TX-2 | 299 | 3354 | 14 | 10 | 12 |  | 290 | 248 | 328 |  | 09.00HRS
|  | SS # 815 | XXX |  | OFF | OFF | OFF |  | XXX
| S/S # 815 | DK-5 Bunglow | XXX |  | 0 | 0 | 0 | 11.01 | XXX
|  | TX-1 | 202 | 21391 | 14 | 15 | 14 |  | 432 | 923 | 364 | 424 | 2024-07-29
|  | TX-2 | 133 | 12050 | 4 | 4 | 5 |  | 100 | 136 | 132 |  | 09.24HRS
|  | DTS # 01 | 505 | 65603 | 19 | 20 | 21 |  | XXX

## 6)RING #6
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
| MAXIMUM DEMAND RECORDING SHEET PAGE: 6 OF 19 | [10 empty] | AUGUST- 2024 |  | PAGE 6 OF 19
RING # 06 (DTS # 02 PNO: A70 & A80)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| WORK SHOP | DTS # 02 | XXX | XXX | 16 | 16 | 16 | 10.83 | XXX
|  | TX-1 | 68 | 7827 | 3 | 3 | 3 |  | 80 | 92 | 72 | 422 | 2024-07-30
|  | TX-2 | 68 | 7810 | 3 | 3 | 3 |  | 72 | 80 | 95 |  | 09.45Hrs
|  | North Coast | XXX |  | 17 | 17 | 15
| North Coast | Work Shop | XXX |  | 17 | 17 | 15 | 10.9
|  | TX-1 | 204 | 15416 | 7 | 7 | 7 |  | 176 | 244 | 180 | 412 | 2024-07-30
|  | TX-2 | 218 | 14766 | 10 | 10 | 8 |  | 348 | 224 | 168 |  | 08.55Hrs
|  | Zone #3 | XXX |  | OFF
| ZONE # 3 | North Coast | XXX |  | 0 | 0 | 0 | 10.79 | XXX
|  | TX-1 | 257 | 3568 | 12 | 12 | 11 |  | 324 | 260 | 272 | 423 | 2024-07-30
|  | TX-2 | 249 | 3022 | 12 | 12 | 12 |  | 312 | 280 | 280 |  | 09.20Hrs
|  | SS Mess | XXX |  | 14 | 15 | 15
| SS MESS | Zone #3 | XXX |  | 16 | 16 | 16 | 10.75 | XXX
|  | TX-1 | 300 | 4107940 | 14 | - | 16 |  | 410 | 440 | 386 | 421 | 2024-07-30
|  | TX-2 | 300 | 4592500 | 16 | - | 16 |  | 448 | 436 | 400 |  | 09.35Hrs
|  | DTS # 02 | XXX | XXX | 48 | 48 | 48 |  | XXX

## 7)RING #7
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
|  |  |  | MAXIMUM DEMAND RECORDING SHEET | [6 empty] | AUGUST - 2024 |  |  | PAGE 7 OF 19
RING # 07 (DTS # 01 PNO: A70 & A80)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| 88-SS-1310 | DTS # 01 | 353 | 73574 | 46 | 43 | 41 | 11.01 | XXX
|  | TX-1 | 350 | 18201 | 10 | 11 | 9 |  | 344 | 236 | 230 | 425 | 2024-07-29
|  | TX-2 | 507 | 19334 | 22 | 22 | 22 |  | 652 | 600 | 625 |  | 8.10 Hrs
|  | S/S # 1320 | XXX |  | 12 | 0 | 0
| 88-SS-1320 | S/S # 1310 | XXX |  | 12 | 0 | 0 | 11 | XXX
|  | TX-1 | 245 | 6274 | 10 | 8 | 9 |  | 265 | 258 | 350 | 424 | 2024-07-29
|  | TX-2 | 71 | 12899 | 0 | 0 | 0 |  | 40 | 40 | 45 |  | 08.35Hrs
|  | S/S # 1420 | XXX |  | 0 | 0 | 0 |  | XXX
| 88-SS-1420 | S/S # 1320 | XXX |  | OFF |  |  | 11 | XXX
|  | TX-1 | 525 | 18847 | 18 | 15 | 17 |  | 440 | 370 | 495 | 421 | 2024-07-29
|  | TX-2 | 218 | 12318 | 5 | 4 | 4 |  | 135 | 75 | 160 |  | 08.45Hrs
|  | S/S # 1410 | XXX |  | 24 | 19 | 22
| 88-SS-1410 | S/S # 1420 | XXX |  | 24 | 19 | 22 | 11 | XXX
|  | TX-1 | 354 | 17892 | 12 | 11 | 10 |  | 364 | 236 | 296 | 420 | 2024-07-29
|  | TX-2 | 175 | 10604 | 5 | 6 | 6 |  | 172 | 188 | 120 |  | 09.00Hrs
|  | DTS # 01 | 1.13 MV | 60246 | 42 | 37 | 38 |  | XXX

## 8)RING #8
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET JULY-2019 PAGE:8 OF 19 | [11 empty] | AUGUST -2024 |  | PAGE 8 OF 19
RING # 08 (DTS # 01 PNO: A110 & A120)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| 88-SS-1510 | DTS # 01 | 918 | 141386 | 35 | 36 | 34 | 11 | XXX
|  | TX-1 | 141 | 32045 | 4 | 5 | 4 |  | 120 | 120 | 75 | 421 | 2024-07-28
|  | TX-2 | 364 | 41792 | 12 | 13 | 11 |  | 355 | 335 | 295 |  | 08.45Hrs
|  | S/S # 1520 | XXX |  | 21 | 21 | 18 |  | XXX
| 88-SS-1520 | S/S # 1510 | XXX |  | 21 | 21 | 19 | 11 | XXX
|  | TX-1 | 224 | 37397 | 8 | 9 | 7 |  | 205 | 185 | 195 | 420 | 2024-07-28
|  | TX-2 | 268 | 30835 | 12 | 12 | 12 |  | 370 | 325 | 315 |  | 09.10Hrs
|  | S/S # 1610 | XXX |  | OFF |  |  |  | XXX
| 88-SS-1610 | S/S # 1520 | XXX |  | 0 | 0 | 0 | 10.9 | XXX
|  | TX-1 | 282 | 34229 | 12 | 12 | 11 |  | 330 | 280 | 370 | 423 | 2024-07-28
|  | TX-2 | 237 | 20098 | 8 | 8 | 8 |  | 205 | 220 | 200 |  | 13.13Hrs
|  | DTS # 01 | 482 | 59478 | 20 | 20 | 19 |  | XXX

## 9)RING #9
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET | [10 empty] | AUGUST - 2024 |  | PAGE 9 OF 19
RING # 09 (DTS # 02 PNO: A110 & A120)
Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
88-SS-1805 | DTS # 02 | 1.02 MV | 76321 | 59 | 54 | 53 | 10.9 | XXX
| TX-1 | 359 | 28052 | 20 | 20 | 21 |  | 409 | 492 | 568 | 422 | 2024-07-28
| TX-2 | 389 | 24724 | 18 | 18 | 21 |  | 423 | 419 | 413 |  | 13.45Hrs
| 88-SS-1810 | XXX |  | 19 | 14 | 13 |  | XXX
88-SS-1810 | 88-SS-1805 | XXX |  | 18 | 15 | 18 | 10.9 | XXX
| TX-1 | 197 | 12445 | 8 | 7 | 6 |  | 256 | 96 | 248 | 419 | 2024-07-28
| TX-2 | 176 | 10364 | 9 | 7 | 5 |  | 3 | 48 | 220 |  | 10.00Hrs
| 88-SS-1710 | XXX |  | OFF |  |  |  | XXX
88-SS-1710 | 88-SS-1810 | XXX |  | 0 | 0 | 0 | 10.9 | XXX
| TX-1 | 268 | 18836 | 10 | 11 | 10 |  | 205 | 185 | 150 | 416
| TX-2 | 190 | 13388 | 8 | 9 | 8 |  | 265 | 180 | 205 | 415 | 2024-07-28
| TX-3 | 217 | 15946 | 11 | 12 | 10 |  | 340 | 275 | 205 | 419 | 10.22Hrs
| TX-4 | 311 | 26376 | 15 | 17 | 16 |  | 415 | 425 | 355 | 417
| 88-SS-550 (New) | XXX |  | 56 | 61 | 10 |  | XXX
| Police Station fdr | 212 | 9242 | 11 | 11 | 10 |  | 210 | 216 | 260 | 421
88-SS-550 (New) | 88-SS-1710 | XXX |  | 57 | 62 | 56 | 10.9
| TX-1 | 788 | 6899093 | 42 | 39 | 39 |  | 1139 | 870 | 930 | 436 | 2024-07-28
| TX-2 | 729 | 5263328 | 34 | 34 | 33 |  | 845 | 820 | 799 |  | 13.28Hrs
| DTS # 02 | 2447 | 9719611 | 126 | 129 | 123

## 10)RING #10
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET | [10 empty] | AUGUST - 2024 |  |  | PAGE 10 OF 19
RING # 10 (DTS # 01 PNO: A130 & A140)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| QPAA 88-SS-0015 | DTS # 01 | 2.11MW | 219890 | 100 | 107 | 182 | 10.9 | XXX |  |  |  | 28/07/2024 08:14Hrs
|  | 88-TR0015-01 | 458 | 18120 | 20 | 21 | 21 |  | 640 | 652 | 646 | 412
|  | 88-TR0015-02 | 577 | 16138 | 30 | 32 | 30 |  | 900 | 848 | 836 | 411
|  | 88-SS-0020 | XXX |  | 100 | 100 | 101 |  | XXX
|  | Desal Plant | 147 | 8308 | 6 | 0 | 0 |  | XXX
|  | DWS Feeder | 454 | 22592 | 20 | 22 | 21 |  | XXX
| QPAA 88-SS-0020 | 88-SS-0015 | XXX |  | 101 | 102 | 100 | 11 | XXX
|  | 88-TR-0020-01 | 314 | 19671 | 12 | 12 | 12 |  | 106 | 94 | 100 | 421 | 29/07/2024 13.25 Hrs
|  | 88-TR-0020-02 | 348 | 21793 | 13 | 15 | 13 |  | 588 | 561 | 541 | 419
|  | IT (86T-SS-8601) | XXX |  | 80 | 80 | 80 |  | XXX
| IT S/S (86T-SS-8601) | 88-SS-0020 | XXX |  | 81 | 80 | 80 | 11.1 | XXX
|  | 86T-TR-8601-01 | 898 | 43994776 | 37 | 39 | 38 |  | 1183 | 1146 | 1198 | 421 | 29/07/2024 13.10Hrs
|  | 86T-TR-8601-02 | 832 | 30396897 | 37 | 39 | 38 |  | 792 | 786 | 751 | 425
|  | HQ (DOMB) | XXX |  | 2 | 2 | 2 |  | XXX
| HQ (DOMB) | IT (86T-SS-8601) | XXX |  |  | OFF |  | 11.01 | XXX
|  | 88-TR002-01 | 700 | 5276 | 7 | 7 | 7 |  | 456 | 452 | 453 | 420 | 30/07/2024 08.40Hrs
|  | 88-TR002-02 | 931 | 1991 | 42 | 43 | 43 |  | 752 | 779 | 761 | 417
|  | 88-TR002-03 | 269 | 3838 | 11 | 11 | 11 |  | 371 | 369 | 338 | 423
|  | 88-TR002-04 | 442 | 1090 | 19 | 19 | 19 |  | 529 | 533 | 540 | 419
|  | DTS # 01 | 1860 | 56690 | 85 | 86 | 86 |  | XXX

## 11)RING #11
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
| MAXIMUM DEMAND RECORDING SHEET | [10 empty] | AUGUST - 2024 | PAGE 11 OF 19
RING # 11 (DTS # 01 PNO: A150 & A160)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| 88-SS-9310 | DTS # 01 | 1595 | 4881189 | 52 | 56 | 58 | 11 | XXX
|  | 88-TR-9310-01 | 472 | 4368335 | 14 | 14 | 14 |  | 359 | 351 | 348 | 439 | 2024-07-30
|  | 88-TR-9310-02 | 334 | 3187812 | 10 | 10 | 10 |  | 247 | 244 | 244 |  | 07.55Hrs
|  | 88-SS-2010 | XXX |  | 30 | 28 | 34 |  | XXX
| 88-SS-2010 | 88-SS-9310 | XXX |  | 28 | 33 | 35 | 11.06 | XXX
|  | 88-TR-2010-01 | 425 | 26599 | 12 | 15 | 16 |  | 328 | 453 | 295 | 427 | 2024-07-30
|  | 88-TR-2010-02 | 492 | 26760 | 16 | 17 | 20 |  | 372 | 533 | 491 |  | 07.41Hrs
|  | 88-SS-2020 | XXX |  | OFF |  |  |  | XXX
| 88-SS-2020 | 88-SS-2010 | XXX |  | 0 | 0 | 0 | 11 | XXX
|  | 88-TR-2020-01 | 392 | 26976 | 11 | 16 | 17 |  | 490 | 514 | 350 | 426 | 2024-07-30
|  | 88-TR-2020-02 | 460 | 28822 | 15 | 17 | 17 |  | 420 | 511 | 410 |  | 08.10Hrs
|  | DTS # 01 | 825 | 55721 | 27 | 32 | 33 |  | XXX

## 12)RING #12
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
|  |  |  | MAXIMUM DEMAND RECORDING SHEET | [6 empty] | AUGUST - 2024 |  |  | PAGE 12 OF 19
RING # 12 (DTS # 02 PNO: A130 & A140)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| 88-SS-9110 (S/S # N1) | DTS # 02 | 786 | 8666563 | 32 | 45 | 43 | 10.9 | XXX
|  | 88-TR-9110-01 | 408 | 2220122 | 13 | 20 | 18 |  | 305 | 669 | 340 | 432 | 2024-07-29
|  | 88-TR-9110-02 | 413 | 2986217 | 15 | 22 | 20 |  | 475 | 714 | 445 |  | 10.15HRS
|  | 88-SS-9120 | XXX |  | 0 | 0 | 0
| 88-SS-9120 (S/S # N2) | 88-SS-9110 | XXX |  | 0FF |  |  | 10.9 | XXX
|  | 88-TR-9120-01 | 337 | 8241133 | 15 | 12 | 18 |  | 394 | 300 | 405 | 430 | 2024-07-29
|  | 88-TR-9120-02 | 314 | 6270723 | 16 | 13 | 14 |  | 394 | 320 | 360 |  | 10.50HRS
|  | DTS # 02 | 627 | 956821 | 31 | 24 | 30 |  | XXX

## 13)RING #14
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
|  |  |  | MAXIMUM DEMAND RECORDING SHEET | [7 empty] | AUGUST - 2024 |  | PAGE 13 OF 19
RING # 14 (DTS # 02 PNO: A170 & A180)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| New Contractor | DTS # 02 | 395 | 6863335 | 18 | 18 | 18 | 10.85 | XXX |  |  |  | 29/07/2024 09.40Hrs
|  | TX-1 | 180 | 5313325 | 9 | 8 | 7 |  | 245 | 170 | 182 | 430
|  | TX-2 | 251 | 8241811 | 10 | 10 | 11 |  | 199 | 299 | 280 | 430
|  | North Gate | XXX |  | OFF
| NEW NORTH GATE | Contractor | XXX |  | 0 | 0 | 0 | 10.86 | 0 |  |  |  | 29/07/2024 09.47Hrs
|  | TX-1 | 165 | 4224943 | 6 | 6 | 6 |  | 149 | 177 | 145 | 430
|  | TX-2 | 166 | 3267248 | 7 | 7 | 6 |  | 182 | 145 | 179
|  | Kathiyah Bypass | 65 | 3619526 | 2 | 2 | 2 |  | XXX
|  | Covenant | XXX |  | 13 | 14 | 13 |  | XXX
| New Covenant | 88-SS-450 | XXX |  | 14 | 15 | 14 | 10.85 | XXX |  |  |  | 29/07/2024 0.9.33Hrs
|  | TX-1 | 175 | 4352101 | 6 | 7 | 6 |  | 183 | 171 | 135 | 430
|  | TX-2 | 349 | 9267622 | 17 | 18 | 15 |  | 479 | 379 | 375
|  | DTS # 02 | 847 | 2382687 | 38 | 41 | 36

## 14)DTS #02 (hidden)
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
|  |  |  | MAXIMUM DEMAND RECORDING SHEET | [6 empty] | SEPTEMBER 2017 |  |  | PAGE 14 OF 18
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [MWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| DTS # 02 | Incomer # 01 | 5012 | 60095 MWH | 290 | 299 | 282 | 10.9 | XXX
|  | 88-TR-0981-01 | 0 | 54 MWH | 0 | 0 | 0 |  | 0 | 0 | 0 | 410 | 28/09/2017
|  | 88-TR-0981-02 | 0 | 318 MWH | 0 | 0 | 0 |  | 100 | 60 | 108 | 410 | 11:00 HRS
|  | Incomer # 02 | 4985 | 59715 MWH | 290 | 308 | 282 |  | XXX
|  | 11KV Ring # 1 (Pnl # A10) | 362 | 6139 MWH | 22 | 21 | 20 |  | XXX
|  | 11KV Ring # 1 (Pnl # A20) | 612 | 9613 MWH | 40 | 34 | 31 |  | XXX
|  | 11KV Ring # 2 (Pnl # A30) | 1842 | 18996 MWH | 107 | 112 | 109 |  | XXX
|  | 11KV Ring # 2 (Pnl # A40) | 386 | 14829 MWH | 24 | 24 | 24 |  | XXX
|  | 11KV Ring # 3 (Pnl # A50) | 359 | 5920 MWH | 18 | 20 | 21 |  | XXX
|  | 11KV Ring # 3 (Pnl # A60) | 1524 | 21698 MWH | 91 | 90 | 86 |  | XXX
|  | 11KV Ring # 6 (Pnl # A70) | 381 | 4836 MWH | 22 | 22 | 18 |  | XXX
|  | 11KV Ring # 6 (Pnl # A80) | 862 | 14019 MWH | 51 | 56 | 58 |  | XXX
|  | 11KV Ring # 9 (Pnl # A110) | 898 | 18128 MWH | 56 | 53 | 47 |  | XXX
|  | 11KV Ring # 9 (Pnl # A120) | 1481 | 13542 MWH | 88 | 91 | 86 |  | XXX
|  | 11KV Ring #12 (Pnl # A130) | 1303 | 2845 MWH | 74 | 79 | 81 |  | XXX
|  | 11KV Ring #12 (Pnl # A140) | 0 | 0 | 0 | 0 | 0 |  | XXX

## 17)DSFA
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
|  |  |  | MAXIMUM DEMAND RECORDING SHEET | [6 empty] | AUGUST - 2024 |  |  | PAGE 17 OF 19
DSFA
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [MWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| 88-SS-1100 | Incomer # 1 | 1.99 MW | 78936 | 707371 | 93 | 91 | 10.9 | XXX |  |  |  | 31/07/2024 13.35Hrs
|  | Ring Fdr # 1 | 968 | 42220 | 45 | 45 | 46 |  | XXX
|  | Al Hamla BH | 767 | 32767 | 26 | 26 | 26 |  | XXX
|  | Coastal RLSS | 51 | 1552 | 1 | 1 | 1 |  | XXX
|  | 88-TR-1100-01 | 34 | 2341 | 0 | 0 | 0 |  | 22 | 15 | 36 | 412
|  | 88-TR-1100-02 | 0 | 2.1 | 0 | 0 | 0 |  | 0 | 0 | 0
|  | Ring Fdr # 2 | 725 | 57579 | 38 | 39 | 37 |  | xxx
|  | Al Hamla RMU | 0 | 2.7 | 0 | 0 | 0 |  | XXX
|  | Incomer # 2 | 724 | 76710 | 39 | 40 | 38 |  | XXX
|  | 86E-TR-0001 | 0 | 57.7 | 0 | 0 | 0 |  | XXX
| 88-SS-1110 | 88-SS-1100 | XXX |  | 55 | 54 | 55 | 10.9 | XXX |  |  |  | 31/07/2024 13.00Hrs
|  | 88-TR-1110-01 | 175 | 381 | 5 | 5 | 5 |  | 147 | 120 | 100 | 417
|  | 88-TR-1110-02 | 194 | 6960 | 5 | 6 | 6 |  | 147 | 147 | 147
|  | 88-SS-1120 | XXX |  | 43 | 44 | 43 |  | XXX
| 88-SS-1120 | 88-SS-1110 | XXX |  | 42 | 41 | 40 | 10.9 | XXX |  |  |  | 30/7/2024 13.5Hrs
|  | 88-TR-1120-01 | 158 | 2421 | 8 | 8 | 8 |  | 190 | 190 | 170 | 410
|  | 88-TR-1120-02 | 66 | 1516 | 2 | 0 | 0 |  | 50 | 48 | 66
|  | 88-SS-1130 | XXX |  | 33 | 32 | 33
| 88-SS-1130 | 88-SS-1120 | XXX |  | 32 | 31 | 31 | 10.9 | XXX |  |  |  | 30/7/2024 13.25Hrs
|  | 88-TR-1130-01 | 112 | 2282 | 2 | 2 | 2 |  | 85 | 110 | 73 | 411
|  | 88-TR-1130-02 | 157 | 1936 | 4 | 4 | 4 |  | 65 | 70 | 73
|  | 88-SS-1140 | XXX |  | 24 | 23 | 23
|  | El Workshop Tx | 0 | 109 | 0 | 0 | 0 |  | XXX
| 88-SS-1140 | 88-SS-1130 | XXX |  | 26 | 25 | 26 | 10.9 | XXX |  |  |  | 30/7/2024 13.00Hrs
|  | 88-TR-1140-01 | 247 | 11059 | 14 | 14 | 15 |  | 380 | 350 | 360 | 408
|  | 88-TR-1140-02 | 181 | 7907 | 10 | 10 | 10 |  | 240 | 254 | 255
|  | 88-SS-0140 | XXX |  | off | off | off |  | XXX
| 88-SS-0140 | 88-SS-1140 | XXX |  | 0 | 0 | 0 | 10.9 | XXX |  |  |  | 31/7/2024 14.00Hrs
|  | 88-TR-0140-01 | 81 | 7301 | 13 | 12 | 13 |  | 85 | 85 | 50 | 418
|  | 88-TR-0140-02 | 27 | 5329 | 9 | 9 | 9 |  | 8 | 7 | 7
|  | 88-SS-0130 | XXX |  | 0 | 0 | 0
| 88-SS-0130 | 88-SS-0140 | XXX |  | 0 | 0 | 0 | 10.9 |  |  |  |  | 31/7/2024 13.47Hrs
|  | 88-TR-0130-01 | 27 | 4793 | 0 | 0 | 0 |  | 12 | 13 | 15 | 420
|  | 88-TR-0130-02 | 264 | 15183 | 15 | 15 | 15 |  | 293 | 285 | 203
|  | 88-SS-1160 | XXX |  | 19 | 21 | 22
| 88-SS-1160 | 88-SS-0130 | XXX |  | 18 | 20 | 17 | 11 | XXX |  |  |  | 31/7/2024 13.15Hrs
|  | 88-TR-1160-01 | 74 | 4829 | 0 | 0 | 0 |  | 25 | 10 | 18 | 414
|  | 88-SS-1150 | XXX |  | 18 | 18 | 21
| 88-SS-1150 | 88-SS-1160 | XXX |  | 19 | 18 | 20 | 10.9 | XXX |  |  |  | 31/7/2024 13.10Hrs
|  | 88-TR-1150-01 | 180 | 10295 | 12 | 12 | 12 |  | 268 | 281 | 240 | 418
|  | 88-TR-1150-02 | 246 | 11842 | 11 | 10 | 10 |  | 328 | 281 | 306
|  | 88-SS-1100 | XXX | XXX | 36 | 39 | 34 |  | XXX