## 1)RING #1
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET
| RING # 01 (DTS # 02 PNO: A10 & A20) | [9 empty] | JUNE - 2024 |  |  | PAGE 1 OF 19
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| Mosque | DTS # 02 | XXX |  | 8 | 8 | 8 | 11.05 | XXX
|  | TX-1 | 200 | 5391270 | 8 | - | 8 |  | 152 | 200 | 200 | 419 | 30/05/2024 10.03Hrs
|  | TX-2 | 150 | 1335340 | 6 | - | 6 |  | 152 | 200 | 200
|  | Fire Station | XXX |  | 0 | 0 | 0 |  | 3
| Fire Station | Mosque | XXX |  | OFF |  |  | 11.03 | XXX |  |  |  | 01/06/2024 08.56Hrs
|  | TX-1 | 281 | 123 | 13 | 9 | 11 |  | 313 | 189 | 325 | 418
TX-2
|  | TX-2 | 192 | 2698 | 8 | 7 | 6 |  | 256 | 142 | 232
|  | Substation#N3 | XXX |  | 21 | 18 | 18
| Substation # N3 | Fire Station | XXX |  | 21 | 18 | 18 | 11.03 | XXX
|  | TX-1 | 41 | 1075647 | 2 | 2 | 2 |  | 12 | 12 | 12 | 437 | 01/06/2024 08.45Hrs
|  | TX-2 | 2 | 399321 | 0 | 0 | 0 |  | 20 | 20 | 19
|  | D-Type | XXX |  | 21 | 18 | 17 |  | XXX
| D-Type | Substation#N3 | XXX |  | 21 | 18 | 17 | 11 | XXX |  |  |  | 01/06/2024 08.35Hrs
|  | TX-1 | 120 | 9673600 | 4 | - | 4 |  | 80 | 128 | 120 | 420
|  | TX-2 | 240 | 9356480 | 8 | - | 8 |  | 80 | 128 | 120
|  | Kahrama PS | 100 | 3453250 | 0 | - | 0 |  | XXX
|  | DTS # 02 | XXX |  | 20 | 24 | 24 |  | XXX

## 2)RING #2
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET
| RING # 02 (DTS # 02 PNO: A30 & A40) | [9 empty] | JUNE - 2024 |  |  | PAGE 2 OF 19
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| Main Camp (New) | DTS # 02 | 125 | 3387516 | 5 | 5 | 5 | 11.04 | XXX
|  | TX-1 | 99 | 3398707 | 4 | 5 | 4 |  | 119 | 104 | 104 | 439 | 30/05/2024 08.40Hrs
|  | TX-2 | 33 | 992846 | 0 | 0 | 0 |  | 0 | 0 | 0
|  | Escarpment | XXX |  | 0 | 0 | 0
| Escarpment | Main Camp New) | XXX |  | OFF |  |  | 11 | XXX
|  | TX-1 | 398 | 21594 | 18 | 18 | 18 |  | 495 | 469 | 468 | 423 | 30/05/2024 08.50Hrs
|  | TX-2 | 469 | 31190 | 17 | 18 | 18 |  | 479 | 461 | 458
|  | SS Bungalow | XXX |  | 36 | 36 | 36
| S.S.Bungalow | Escarpment | XXX |  | 36 | 36 | 36 | 11 | XXX
|  | TX-1 | 180 | 253610 | 6 | - | 6 |  | 148 | 152 | 152 | 411 | 30/05/2024 08.20Hrs
|  | TX-2 | 170 | 284240 | 5 | - | 6 |  | 142 | 146 | 149
|  | Supalite | XXX |  | 36 | 40 | 36
| Supalite | SS Bungalow | XXX |  |  |  |  | - | XXX
|  | TX-1 | 279 | 33181483 | XXX |  |  |  | 208 | 268 | 280 | 410 | 30/05/2024 08.12Hrs
|  | TX-2 | 268 | 31867645 | XXX |  |  |  | 207 | 254 | 282
|  | DTS # 02 | XXX | [5 empty] | XXX

## 3)RING #3
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET
| RING # 03 (DTS # 02 PNO: A50 & A60) | [9 empty] | JUNE - 2024 |  |  | PAGE 3 OF 19
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| Hospital | DTS # 02 | 734 | 78796 | 33 | 35 | 33 | 11.04 | XXX
|  | TX-1 | 313 | 9884 | 8 | 10 | 8 |  | 259 | 217 | 215 | 418 | 2024-06-01
|  | TX-2 | 214 | 4019 | 4 | 4 | 4 |  | 120 | 121 | 125 |  | 09.47HRS
|  | New Cinema | XXX |  | 22 | 23 | 23 |  | XXX
| New Cinema | Hospital | XXX |  | 23 | 23 | 23 | 11.01 | XXX
|  | TX-1 | 325 | 6783546 | 16 | 16 | 16 |  | 415 | 420 | 405 | 435 | 2024-06-01
|  | TX-2 | 141 | 3675640 | 6 | 6 | 6 |  | 185 | 164 | 164 | 437 | 09.36HRS
|  | New M.R.Club | XXX |  | 0 | 0 | 0 |  | XXX
| New M.R. Club | New Cinema | XXX |  | OFF |  |  | 11.01 | XXX
|  | TX-1 | 646 | 2783486 | 29 | 31 | 28 |  | 888 | 763 | 751 | 434 | 2024-06-01
|  | TX-2 | 723 | 5355730 | 36 | 37 | 34 |  | 995 | 867 | 827 | 435 | 13.40HRS
|  | DTS # 2 | 1298 | 7119189 | 63 | 67 | 61 |  | XXX

## 4)RING #4
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET
| RING # 04 (DTS # 01 PNO: A30 & A40) | [9 empty] | JUNE - 2024 |  |  | PAGE 4 OF 19
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| F/Ball Pitch | DTS # 01 | 440 | 68181500 | 9 | - | 8 | 10.98 | XXX
|  | TX-1 | 100 | 230130 | 4 | - | 3 |  | 28 | 28 | 28 | 410 | 2024-06-01
|  | TX-2 | 120 | 5152440 | 5 | - | 4 |  | 91 | 98 | 126 |  | 10.02HRS
|  | Dk-5 | XXX |  | OFF
| DK-5 | Football Pitch | XXX |  | 0 | 0 | 0 | 10.9 | XXX
|  | TX-1 | 180 | 9044960 | 7 | - | 8 |  | 105 | 91 | 98 | 415 | 2024-06-01
|  | TX-2 | 180 | 9551510 | 8 | - | 6 |  | 203 | 231 | 230 |  | 10.10HRS
|  | DTS # 01 | XXX |  | 8 | 8 | 8 |  | XXX

## 5)RING #5
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET
| RING # 05 (DTS # 01 PNO: A50 & A60) | [9 empty] | JUNE - 2024 |  |  | PAGE 5 OF 19
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| Dk5 Bungalows | DTS # 01 | 0 | 1327 | 16 | 11 | 14 | 11.03 | XXX
|  | TX-1 | 119 | 8822 | 4 | 5 | 5 |  | 83 | 65 | 143 | 408 | 2024-06-02
|  | TX-2 | 242 | 3079 | 10 | 9 | 8 |  | 257 | 214 | 342 |  | 09.52HRS
|  | SS # 815 | XXX |  | OFF | OFF | OFF |  | XXX
| S/S # 815 | DK-5 Bunglow | XXX |  | 0 | 0 | 0 | 10.9 | XXX
|  | TX-1 | 297 | 21012 | 11 | 12 | 11 |  | 304 | 276 | 276 | 420 | 2024-06-02
|  | TX-2 | 113 | 11926 | 4 | 0 | 4 |  | 100 | 80 | 104 |  | 09.37HRS
|  | DTS # 01 | 469 | 65098 | 14 | 17 | 15 |  | XXX

## 6)RING #6
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
| MAXIMUM DEMAND RECORDING SHEET PAGE: 6 OF 19 | [10 empty] | JUNE - 2024 |  | PAGE 6 OF 19
RING # 06 (DTS # 02 PNO: A70 & A80)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| WORK SHOP | DTS # 02 | XXX | XXX | 12 | 12 | 12 | 11.05 | XXX
|  | TX-1 | 65 | 7799 | 3 | 3 | 3 |  | 70 | 66 | 66 | 422 | 2024-05-30
|  | TX-2 | 66 | 7782 | 3 | 3 | 3 |  | 70 | 64 | 88 |  | 09.30Hrs
|  | North Coast | XXX |  | 15 | 14 | 14
| North Coast | Work Shop | XXX |  | 15 | 13 | 0 | 11
|  | TX-1 | 194 | 15201 | 5 | 5 | 4 |  | 156 | 128 | 128 | 423 | 2024-05-30
|  | TX-2 | 205 | 14534 | 9 | 9 | 6 |  | 320 | 176 | 176 |  | 08.58Hrs
|  | Zone #3 | XXX |  | OFF
| ZONE # 3 | North Coast | XXX |  | 0 | 0 | 0 | 11.07 | XXX
|  | TX-1 | 244 | 3318 | 11 | 11 | 10 |  | 260 | 216 | 202 | 425 | 2024-05-30
|  | TX-2 | 238 | 2780 | 10 | 11 | 10 |  | 230 | 200 | 200 |  | 09.09Hrs
|  | SS Mess | XXX |  | 12 | 12 | 12
| SS MESS | Zone #3 | XXX |  | 12 | 12 | 12 | 11 | XXX
|  | TX-1 | 330 | 3788210 | 14 | 14 | 13 |  | 400 | 400 | 371 | 420 | 2024-05-30
|  | TX-2 | 330 | 4268900 | 15 | 14 | 15 |  | 400 | 425 | 371 |  | 09.19Hrs
|  | DTS # 02 | XXX | XXX | 46 | 44 | 42 |  | XXX

## 7)RING #7
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
|  |  |  | MAXIMUM DEMAND RECORDING SHEET | [6 empty] | JUNE - 2024 |  |  | PAGE 7 OF 19
RING # 07 (DTS # 01 PNO: A70 & A80)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| 88-SS-1310 | DTS # 01 | 1.47MW | 72555 | 38 | 37 | 33 | 11 | XXX
|  | TX-1 | 218 | 17949 | 9 | 8 | 7 |  | 268 | 116 | 164 | 424 | 2024-05-29
|  | TX-2 | 455 | 18868 | 20 | 18 | 19 |  | 580 | 504 | 632 |  | 10.12Hrs
|  | S/S # 1320 | XXX |  | 0 | 0 | 0
| 88-SS-1320 | S/S # 1310 | XXX |  | 0 | 0 | 0 | 11 | XXX
|  | TX-1 | 205 | 6017 | 7 | 6 | 7 |  | 220 | 205 | 225 | 424 | 2024-05-29
|  | TX-2 | 57 | 12855 | 0 | 0 | 0 |  | 40 | 40 | 55 |  | 10.33Hrs
|  | S/S # 1420 | XXX |  | 0 | 0 | 0 |  | XXX
| 88-SS-1420 | S/S # 1320 | XXX |  | OFF |  |  | 11 | XXX
|  | TX-1 | 433 | 18283 | 13 | 12 | 12 |  | 340 | 310 | 350 | 424 | 2024-05-29
|  | TX-2 | 198 | 12134 | 8 | 7 | 7 |  | 210 | 160 | 240 |  | 10.30Hrs
|  | S/S # 1410 | XXX |  | 22 | 19 | 20
| 88-SS-1410 | S/S # 1420 | XXX |  | 23 | 21 | 21 | 11 | XXX
|  | TX-1 | 311 | 17535 | 10 | 8 | 8 |  | 276 | 176 | 224 | 422 | 2024-05-29
|  | TX-2 | 139 | 10421 | 4 | 5 | 5 |  | 120 | 136 | 120 |  | 10.20Hrs
|  | DTS # 01 | 1.35MW | 58964 | 37 | 34 | 34 |  | XXX

## 8)RING #8
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET JULY-2019 PAGE:8 OF 19 | [11 empty] | JUNE -2024 |  | PAGE 8 OF 19
RING # 08 (DTS # 01 PNO: A110 & A120)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| 88-SS-1510 | DTS # 01 | 1.02MW | 140324 | 29 | 34 | 28 | 11 | XXX
|  | TX-1 | 129 | 31894 | 4 | 5 | 5 |  | 125 | 140 | 110 | 422 | 2024-05-29
|  | TX-2 | 309 | 41414 | 9 | 11 | 9 |  | 325 | 295 | 210 |  | 08.11Hrs
|  | S/S # 1520 | XXX |  | 14 | 17 | 14 |  | XXX
| 88-SS-1520 | S/S # 1510 | XXX |  | 16 | 19 | 15 | 11 | XXX
|  | TX-1 | 169 | 37161 | 5 | 7 | 6 |  | 155 | 185 | 90 | 421 | 2024-05-29
|  | TX-2 | 243 | 30541 | 10 | 12 | 9 |  | 350 | 300 | 225 |  | 07.48Hrs
|  | S/S # 1610 | XXX |  | OFF |  |  |  | XXX
| 88-SS-1610 | S/S # 1520 | XXX |  | 0 | 0 | 0 | 11 | XXX
|  | TX-1 | 245 | 33911 | 10 | 11 | 11 |  | 265 | 345 | 285 | 424 | 2024-05-29
|  | TX-2 | 231 | 19893 | 7 | 7 | 7 |  | 185 | 190 | 190 |  | 14.00Hrs
|  | DTS # 01 | 848 | 58955 | 17 | 18 | 19 |  | XXX

## 9)RING #9
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET | [10 empty] | JUNE - 2024 |  | PAGE 9 OF 19
RING # 09 (DTS # 02 PNO: A110 & A120)
Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
88-SS-1805 | DTS # 02 | 912 | 75146 | 41 | 42 | 35 | 10.9 | XXX
| TX-1 | 321 | 27678 | 14 | 16 | 16 |  | 434 | 430 | 421 | 424 | 2024-05-29
| TX-2 | 334 | 24324 | 15 | 16 | 14 |  | 390 | 319 | 356 |  | 10.24Hrs
| 88-SS-1810 | XXX |  | 12 | 0 | 0 |  | XXX
88-SS-1810 | 88-SS-1805 | XXX |  | 12 | 0 | 0 | 11 | XXX
| TX-1 | 168 | 12237 | 6 | 5 | 4 |  | 184 | 60 | 128 | 421 | 2024-05-29
| TX-2 | 156 | 10171 | 5 | 4 | 0 |  | 186 | 40 | 100 |  | 10.12Hrs
| 88-SS-1710 | XXX |  | OFF |  |  |  | XXX
88-SS-1710 | 88-SS-1810 | XXX |  | 0 | 0 | 0 | 11 | XXX
| TX-1 | 200 | 18686 | 10 | 11 | 10 |  | 325 | 320 | 281 | 419
| TX-2 | 252 | 13191 | 6 | 7 | 6 |  | 205 | 180 | 120 | 419 | 2024-05-29
| TX-3 | 241 | 15745 | 13 | 13 | 12 |  | 375 | 305 | 295 | 419 | 10.02Hrs
| TX-4 | 282 | 26065 | 14 | 15 | 14 |  | 410 | 420 | 350 | 420
| 88-SS-550 (New) | XXX |  | 54 | 59 | 54 |  | XXX
| Police Station fdr | 187 | 9004 | 10 | 11 | 10 |  | 200 | 280 | 279 | 420
88-SS-550 (New) | 88-SS-1710 | XXX |  | 52 | 56 | 51 | 11.01
| TX-1 | 785 | 6029317 | 34 | 33 | 34 |  | 885 | 770 | 830 | 436 | 2024-05-29
| TX-2 | 786 | 4567029 | 34 | 35 | 36 |  | 885 | 830 | 805 |  | 10.42Hrs
| DTS # 02 | 2432 | 7050484 | 114 | 119 | 114

## 10)RING #10
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
MAXIMUM DEMAND RECORDING SHEET | [10 empty] | JUNE - 2024 |  |  | PAGE 10 OF 19
RING # 10 (DTS # 01 PNO: A130 & A140)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| QPAA 88-SS-0015 | DTS # 01 | 2.4MW | 211198 | 162 | 157 | 166 | 10.9 | XXX |  |  |  | 02/06/2024 10.42Hrs
|  | 88-TR0015-01 | 391 | 17710 | 21 | 22 | 22 |  | 616 | 620 | 600 | 411
|  | 88-TR0015-02 | 511 | 15997 | 30 | 31 | 30 |  | 812 | 719 | 761 | 410
|  | 88-SS-0020 | XXX |  | 94 | 95 | 94 |  | XXX
|  | Desal Plant | 131 | 8171 | 6 | 0 | 0 |  | XXX
|  | DWS Feeder | 406 | 22159 | 15 | 17 | 17 |  | XXX
| QPAA 88-SS-0020 | 88-SS-0015 | XXX |  | 97 | 98 | 97 | 10.9 | XXX
|  | 88-TR-0020-01 | 293 | 19441 | 5 | 4 | 4 |  | 111 | 109 | 95 | 419 | 02/06/2024 10.47Hrs
|  | 88-TR-0020-02 | 311 | 21553 | 21 | 22 | 20 |  | 588 | 561 | 541 | 419
|  | IT (86T-SS-8601) | XXX |  | 72 | 71 | 71 |  | XXX
| IT S/S (86T-SS-8601) | 88-SS-0020 | XXX |  | 72 | 71 | 72 | 11.01 | XXX
|  | 86T-TR-8601-01 | 864 | 43197554 | 45 | 44 | 45 |  | 1183 | 1146 | 1198 | 421 | 02/06/2024 10.57Hrs
|  | 86T-TR-8601-02 | 621 | 29707463 | 29 | 29 | 29 |  | 792 | 786 | 751 | 425
|  | HQ (DOMB) | XXX |  | 24 | 24 | 24 |  | XXX
| HQ (DOMB) | IT (86T-SS-8601) | XXX |  | 1 | 2 | 1 | 11.01 | XXX
|  | 88-TR002-01 | 574 | 4895 | 17 | 17 | 17 |  | 456 | 452 | 453 | 420 | 02/06/2024 10:22Hrs
|  | 88-TR002-02 | 789 | 1387 | 28 | 29 | 29 |  | 752 | 779 | 761 | 417
|  | 88-TR002-03 | 273 | 3563 | 12 | 11 | 12 |  | 371 | 369 | 338 | 423
|  | 88-TR002-04 | 439 | 641 | 21 | 20 | 21 |  | 529 | 533 | 540 | 419
|  | DTS # 01 | 3550 | 54974 | 78 | 80 | 80 |  | XXX

## 11)RING #11
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
| MAXIMUM DEMAND RECORDING SHEET | [10 empty] | JUNE - 2024 | PAGE 11 OF 19
RING # 11 (DTS # 01 PNO: A150 & A160)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| 88-SS-9310 | DTS # 01 | 1594 | 3300493 | 63 | 63 | 67 | 11.06 | XXX
|  | 88-TR-9310-01 | 315 | 4022268 | 16 | 16 | 16 |  | 379 | 375 | 375 | 441 | 2024-05-30
|  | 88-TR-9310-02 | 287 | 2960626 | 14 | 14 | 14 |  | 375 | 371 | 371 |  | 13.01Hrs
|  | 88-SS-2010 | XXX |  | 33 | 34 | 38 |  | XXX
| 88-SS-2010 | 88-SS-9310 | XXX |  | 33 | 35 | 38 | 11 | XXX
|  | 88-TR-2010-01 | 406 | 26146 | 13 | 15 | 18 |  | 333 | 526 | 409 | 428 | 2024-05-30
|  | 88-TR-2010-02 | 465 | 26212 | 19 | 19 | 20 |  | 506 | 546 | 514 |  | 13.15Hrs
|  | 88-SS-2020 | XXX |  | OFF |  |  |  | XXX
| 88-SS-2020 | 88-SS-2010 | XXX |  | 0 | 0 | 0 | 11 | XXX
|  | 88-TR-2020-01 | 416 | 26531 | 15 | 19 | 18 |  | 428 | 555 | 333 | 428 | 2024-05-30
|  | 88-TR-2020-02 | 431 | 28313 | 15 | 19 | 19 |  | 438 | 571 | 403 |  | 12.54Hrs
|  | DTS # 01 | 1.47MW | 54770 | 31 | 39 | 37 |  | XXX

## 12)RING #12
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
|  |  |  | MAXIMUM DEMAND RECORDING SHEET | [6 empty] | JUNE - 2024 |  |  | PAGE 12 OF 19
RING # 12 (DTS # 02 PNO: A130 & A140)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| 88-SS-9110 (S/S # N1) | DTS # 02 | 753 | 7781777 | 25 | 36 | 35 | 11.09 | XXX
|  | 88-TR-9110-01 | 378 | 1768570 | 13 | 17 | 16 |  | 305 | 550 | 380 | 431 | 2024-05-30
|  | 88-TR-9110-02 | 377 | 2551042 | 12 | 19 | 18 |  | 340 | 620 | 315 |  | 10.03Hrs
|  | 88-SS-9120 | XXX |  | 0 | 0 | 0
| 88-SS-9120 (S/S # N2) | 88-SS-9110 | XXX |  | 0FF |  |  | 11.04 | XXX
|  | 88-TR-9120-01 | 298 | 7879478 | 15 | 11 | 13 |  | 355 | 245 | 364 | 438 | 2024-05-30
|  | 88-TR-9120-02 | 294 | 5949368 | 14 | 11 | 13 |  | 350 | 230 | 390 |  | 10.15Hrs
|  | DTS # 02 | 585 | 275326 | 29 | 23 | 24 |  | XXX

## 13)RING #14
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
|  |  |  | MAXIMUM DEMAND RECORDING SHEET | [7 empty] | JUNE - 2024 |  | PAGE 13 OF 19
RING # 14 (DTS # 02 PNO: A170 & A180)
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [kWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| New Contractor | DTS # 02 | 389 | 6428603 | 18 | 19 | 18 | 11.03 | XXX |  |  |  | 01/06/2024 09.14Hrs
|  | TX-1 | 168 | 5156258 | 7 | 7 | 7 |  | 212 | 167 | 170 | 437
|  | TX-2 | 244 | 7964101 | 10 | 11 | 10 |  | 280 | 312 | 235 | 437
|  | North Gate | XXX |  | OFF
| NEW NORTH GATE | Contractor | XXX |  | 0 | 0 | 0 | 11.01 | 0 |  |  |  | 01/06/2024 09.26Hrs
|  | TX-1 | 154 | 4079851 | 7 | 7 | 7 |  | 170 | 194 | 172 | 436
|  | TX-2 | 124 | 3151281 | 6 | 5 | 5 |  | 134 | 117 | 110
|  | Kathiyah Bypass | 60 | 3560483 | 1 | 1 | 1 |  | XXX
|  | Covenant | XXX |  | 17 | 14 | 12 |  | XXX
| New Covenant | 88-SS-450 | XXX |  | 12 | 12 | 12 | 11.01 | XXX |  |  |  | 01/06/2024 09.04Hrs
|  | TX-1 | 151 | 4188757 | 6 | 6 | 6 |  | 155 | 163 | 171 | 437
|  | TX-2 | 306 | 8901915 | 13 | 14 | 11 |  | 379 | 299 | 320
|  | DTS # 02 | 730 | 1534032 | 31 | 32 | 30

## 14)DTS #02 (hidden)
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
|  |  |  | MAXIMUM DEMAND RECORDING SHEET | [6 empty] | SEPTEMBER 2017 |  |  | PAGE 14 OF 18
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [MWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| DTS # 02 | Incomer # 01 | 5012 | 60095 MWH | 290 | 299 | 282 | 10.9 | XXX
|  | 88-TR-0981-01 | 0 | 54 MWH | 0 | 0 | 0 |  | 0 | 0 | 0 | 410 | 28/09/2017
|  | 88-TR-0981-02 | 0 | 318 MWH | 0 | 0 | 0 |  | 100 | 60 | 108 | 410 | 11:00 HRS
|  | Incomer # 02 | 4985 | 59715 MWH | 290 | 308 | 282 |  | XXX
|  | 11KV Ring # 1 (Pnl # A10) | 362 | 6139 MWH | 22 | 21 | 20 |  | XXX
|  | 11KV Ring # 1 (Pnl # A20) | 612 | 9613 MWH | 40 | 34 | 31 |  | XXX
|  | 11KV Ring # 2 (Pnl # A30) | 1842 | 18996 MWH | 107 | 112 | 109 |  | XXX
|  | 11KV Ring # 2 (Pnl # A40) | 386 | 14829 MWH | 24 | 24 | 24 |  | XXX
|  | 11KV Ring # 3 (Pnl # A50) | 359 | 5920 MWH | 18 | 20 | 21 |  | XXX
|  | 11KV Ring # 3 (Pnl # A60) | 1524 | 21698 MWH | 91 | 90 | 86 |  | XXX
|  | 11KV Ring # 6 (Pnl # A70) | 381 | 4836 MWH | 22 | 22 | 18 |  | XXX
|  | 11KV Ring # 6 (Pnl # A80) | 862 | 14019 MWH | 51 | 56 | 58 |  | XXX
|  | 11KV Ring # 9 (Pnl # A110) | 898 | 18128 MWH | 56 | 53 | 47 |  | XXX
|  | 11KV Ring # 9 (Pnl # A120) | 1481 | 13542 MWH | 88 | 91 | 86 |  | XXX
|  | 11KV Ring #12 (Pnl # A130) | 1303 | 2845 MWH | 74 | 79 | 81 |  | XXX
|  | 11KV Ring #12 (Pnl # A140) | 0 | 0 | 0 | 0 | 0 |  | XXX

## 17)DSFA
INDUSTRIAL CITY OPERATIONS (DCA)
UTILITIES (DISTRIBUTION)
|  |  |  | MAXIMUM DEMAND RECORDING SHEET | [6 empty] | JUNE - 2024 |  |  | PAGE 17 OF 19
DSFA
| Substation | Ring/Feeder | Maximum Demand [kW] | Energy Meter Reading [MWh] | Load Current Reading [Amp] R Y B |  |  | Voltage [kV] | Load Current Reading [Amp] R Y B |  |  | Voltage [V] | Time & Date | Remarks
| 88-SS-1100 | Incomer # 1 | 1.8MW | 77332 | 69 | 71 | 69 | 10.8 | XXX |  |  |  | 02/06/2024 07.45Hrs
|  | Ring Fdr # 1 | 955 | 41405 | 49 | 51 | 50 |  | XXX
|  | Al Hamla BH | 967 | 32038 | 29 | 29 | 29 |  | XXX
|  | Coastal RLSS | 46 | 1524 | 1 | 1 | 1 |  | XXX
|  | 88-TR-1100-01 | 25 | 2311 | 0 | 0 | 0 |  | 20 | 12 | 38 | 412
|  | 88-TR-1100-02 | 0 | 2.1 | 0 | 0 | 0 |  | 0 | 0 | 0
|  | Ring Fdr # 2 | 711 | 56789 | 34 | 35 | 32 |  | xxx
|  | Al Hamla RMU | 0 | 2.7 | 0 | 0 | 0 |  | XXX
|  | Incomer # 2 | 713 | 75916 | 33 | 34 | 33 |  | XXX
|  | 86E-TR-0001 | 191 | 51 | 0 | 0 | 0 |  | XXX
| 88-SS-1110 | 88-SS-1100 | XXX |  | 47 | 48 | 48 | 10.8 | XXX |  |  |  | 02/06/2024 08.00Hrs
|  | 88-TR-1110-01 | 202 | 312 | 5 | 5 | 6 |  | 119 | 169 | 169 | 408
|  | 88-TR-1110-02 | 147 | 6850 | 4 | 5 | 5 |  | 119 | 146 | 85
|  | 88-SS-1120 | XXX |  | 37 | 38 | 38 |  | XXX
| 88-SS-1120 | 88-SS-1110 | XXX |  | 40 | 41 | 41 | 10.8 | XXX |  |  |  | 02/06/2024 08.30Hrs
|  | 88-TR-1120-01 | 148 | 2348 | 8 | 8 | 8 |  | 169 | 169 | 189 | 408
|  | 88-TR-1120-02 | 75 | 1481 | 0 | 0 | 0 |  | 84 | 78 | 63
|  | 88-SS-1130 | XXX |  | 31 | 32 | 31
| 88-SS-1130 | 88-SS-1120 | XXX |  | 29 | 30 | 29 | 10.8 | XXX |  |  |  | 02/06/2024 08.20Hrs
|  | 88-TR-1130-01 | 97 | 2221 | 3 | 3 | 2 |  | 81 | 81 | 63 | 410
|  | 88-TR-1130-02 | 145 | 1870 | 3 | 4 | 3 |  | 108 | 96 | 90
|  | 88-SS-1140 | XXX |  | 22 | 23 | 23
|  | El Workshop Tx | 0 | 106 | 0 | 0 | 0 |  | XXX
| 88-SS-1140 | 88-SS-1130 | XXX |  | 22 | 23 | 23 | 10.9 | XXX |  |  |  | 02/06/2024 08.35Hrs
|  | 88-TR-1140-01 | 251 | 10821 | 13 | 14 | 14 |  | 317 | 317 | 317 | 409
|  | 88-TR-1140-02 | 182 | 7753 | 9 | 9 | 9 |  | 224 | 224 | 240
|  | 88-SS-0140 | XXX |  | off | off | off |  | XXX
| 88-SS-0140 | 88-SS-1140 | XXX |  | 0 | 0 | 0 | 10.9 | XXX |  |  |  | 02/06/2024 09.10Hrs
|  | 88-TR-0140-01 | 82 | 7220 | 3 | 3 | 3 |  | 88 | 84 | 92 | 410
|  | 88-TR-0140-02 | 27 | 5309 | 0 | 0 | 0 |  | 10 | 12 | 10
|  | 88-SS-0130 | XXX |  | 0 | 0 | 0
| 88-SS-0130 | 88-SS-0140 | XXX |  | 0 | 0 | 0 | 10.9 |  |  |  |  | 02/06/2024 09.20Hrs
|  | 88-TR-0130-01 | 28 | 4773 | 0 | 0 | 0 |  | 9 | 6 | 12 | 411
|  | 88-TR-0130-02 | 258 | 14941 | 10 | 10 | 10 |  | 270 | 270 | 195
|  | 88-SS-1160 | XXX |  | 13 | 14 | 13
| 88-SS-1160 | 88-SS-0130 | XXX |  | 13 | 13 | 13 | 10.8 | XXX |  |  |  | 02/06/2024 07.10Hrs
|  | 88-TR-1160-01 | 61 | 4780 | 0 | 0 | 0 |  | 20 | 6 | 22 | 411
|  | 88-SS-1150 | XXX |  | 14 | 14 | 14
| 88-SS-1150 | 88-SS-1160 | XXX |  | 14 | 14 | 14 | 10.7 | XXX |  |  |  | 02/06/2024 07.22Hrs
|  | 88-TR-1150-01 | 185 | 10137 | 6 | 6 | 5 |  | 169 | 146 | 120 | 406
|  | 88-TR-1150-02 | 243 | 11616 | 13 | 13 | 12 |  | 339 | 317 | 328
|  | 88-SS-1100 | XXX | XXX | 35 | 35 | 34 |  | XXX